## MEASUREMENTS
BOILER WATER TREATMENT PROGRAM (PRINTED LOGS)
VESSEL NAME: | [6 empty] | COMPANY NAME: | [10 empty] | MONTH: | [7 empty] | YEAR:
TESTED BY: | [6 empty] | CHIEF ENG.: | [10 empty] | BOILER PRESSURE:
ENGINE TYPE: | [6 empty] | SYSTEM CAPACITY:
CHEMICALS ON BOARD | FOS CONDENSAMINE, OXYAMINE | [9 empty] | MAKE UP WATER SOURCE: |  |  |  | SHORE
* Kindly log your results, below in ppm
TEST TO BE CARRIED OUT EVERY 24 HOURS / 48 HOURS (please choose)
DATE (DAY OF MONTH) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
P - Alkalinity in ppm. (Normal range 150-300 ppm)
FOS CONDENSAMINE Dosage in ltr. (see initial dosage instructions)
DEHA IN ppm. (Normal range 0.1-0.4)
OXYAMINE Dosage in ltr. (see initial dosage instructions)
REFERENCE VALUES
Phosphate in ppm. (Normal range 20-50 ppm)
NEUTRALIZED CONDUCTIVITY μS/cm ( < 700 μS/cm)
Chloride in ppm / Normal range < 200 ppm
MAKEUP WATER USAGE in ltr.
Chloride (makeup water) in ppm (reference)
Hardness (makeup water) in ppm (reference)
Blowdown (in sec)
Hotwell temperature (°C)
pH (Boiler) (9.5-11.5)
pH (Hotwell Tank Boiler Feedwater) (8.5-9.5)
pH in condensate water ( 8.2 - 9.2)
Comments:
[15 empty] | Checked By: | [10 empty] | Chief Engineer:

## DOSING AND ADJUSTMENTS
SOLUTIONS
FOS CONDENSAMINE
"P" Alkalinity ppm CaCO3 | 0 | 50 | 100 | 150 | 200 | 225 | 250 | 300 | 350
FOS CONDENSAMINE L/1000 L | 2,5 | 1.9 | 1,3 | 0,7 | 0 | 0 | 0 | 0 | BLD
OXYAMINE
DEHA test results in ppm
0.00 – 0.1 | 0.1 – 0.4 | +0.40
Increase dose by 25% and retest | Maintain dose | Decrease dose by 25% and retest
CONDENSAMINE
Condensate pH form testing
All Boiler
Systems | Less than 8.3 | 8.3 – 9 | 9.0 +
| Increase Dosage by 25% for 72 hours and retest. | Satisfactory maintain dosage | Decrease dosage by 25% for 72 hour and retest
KEM HARD LIQUID
Pressure range |  | Phosphate test result in ppm PO4 Standard | [5 empty] | Phosphate Initial Range (ppm) | Initial Dose milliliters/ Tonne
0-10 10-20 20-30 30-40 40-50 50 +
0-40 Bar | Dose of kem hard liquid milliliters per Tonne of water | 130 | 100 | Satisfactory | Satisfactory | Satisfactory | Blowdown | 20 - 50 | 130
0-588 Psi
41-60 Bar |  | 60 | 30 | Satisfactory | Blowdown | Blowdown | Blowdown | 15 - 30 | 60
603-880 Psi
> 60 Bar |  | 50 | Satisfactory | Satisfactory | Blowdown | Blowdown | Blowdown | 10 - 25 | 50
>880 Psi