## MEASUREMENTS
COOLING WATER TREATMENT PROGRAM
VESSEL NAME: | [6 empty] | COMPANY NAME: | [10 empty] | MONTH: | [7 empty] | YEAR:
TESTED BY: | [6 empty] | CH. ENG.:
MAKER: | [7 empty] | SYSTEM CAPACITY:
CHEMICALS ON BOARD | ADICO NC-L | [9 empty] | MAKE UP WATER SOURCE: |  |  |  | SHORE
* Kindly log your results, below in ppm
System #1 | TEST TO BE CARRIED OUT EVERY ONE (1) TIME PER WEEK (please indicate date)
DATE (DAY OF MONTH) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Nitrite in ppm. (Normal range 1250-3000 ppm)
ADICO NC-L Dosage in ltr. (see initial dosage instructions)
System Water Chloride in ppm / Normal range 0-50 ppm
MAKEUP WATER USAGE in ltr.
pH / Normal Range 8.30-10
Conductivity ( uS/cm ) / Normal Range 3000-5000 uS/cm
Comments:
System #2 | TEST TO BE CARRIED OUT EVERY ONE (1) TIME PER WEEK (please indicate date)
DATE (DAY OF MONTH) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Nitrite in ppm. (Normal range 1250-3000 ppm)
ADICO NC-L Dosage in ltr. (see initial dosage instructions)
System Water Chloride in ppm / Normal range 0-50 ppm
MAKEUP WATER USAGE in ltr.
pH / Normal Range 8.30-10
Conductivity ( uS/cm ) / Normal Range 3000-5000 uS/cm
Comments:
*In case there are more systems involved, please contact our tech dept. | [14 empty] | Checked By: | [10 empty] | Chief Engineer:

## DOSING AND ADJUSTMENTS
Solutions
ADICO NC-L
Nitrite test results in ppm
NITRITE ppm NO2 | 0 | 250 | 500 | 750 | 1000 | 1250 | 1500 | 2000 | 3000 | 4000
ADICO NC L LT/1000lt. | 10 | 9 | 7 | 5 | 3 | 2 | 0 | 0 | 0 | 0