## Worksheet
Date | Subscriber's name | Daily measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-03-27 | Zhytnitskyi Vitalii | 2026-03-27 | 0,2 |  | 180 |  | 20 | 700 | 10 | 300 | 0 | 0 | 120 | 85 | 9,5 | 8,7 | 8,5
2026-03-20 | Zhytnitskyi Vitalii | 2026-03-20 | 0,2 |  | 160 |  | 20 | 700 | 10 | 300 | 0 | 0 | 120 | 80 | 9,5 | 8,7 | 8,5
2026-03-14 | Zhytnitskyi Vitalii | 2026-03-13 | 0,2 |  | 160 |  | 20 | 700 | 10 | 300 | 0 | 0 | 120 | 82 | 9,5 | 8,7 | 8,5
2026-03-09 | Zhytnitskyi Vitalii | 2026-03-06 | 0,1 |  | 180 |  | 20 | 700 | 10 | 300 | 0 | 0 | 120 | 80 | 9,5 | 8,7 | 8,5