## Worksheet
Date | Subscriber's name | Daily measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-05-01 | Martin Schulte | 2026-04-26 | 0,1 |  | 150 | 3 |  |  | 20 | 200 | 10 |  | 30 | 89 | 10 | 9 | 9
2026-05-01 | Martin Schulte | 2026-04-19 | 0,05 | 2 | 150 | 6 |  |  | 20 | 200 | 10 |  | 30 | 80 | 10 | 9 | 9
2026-04-23 | MARTIN SCHULTE | 2026-04-05 | 0,2 |  | 130 | 6 |  |  | 20 | 300 | 0 |  | 20 | 78 | 10 | 8,5 | 8,5
2026-04-23 | MARTIN SCHULTE | 2026-04-12 | 0,1 |  | 150 | 6 |  |  | 20 | 300 | 20 |  | 15 | 80 | 10 | 9 | 8,5
2026-04-05 | MARTIN SCHULTE | 2026-03-29 | 0,1 |  | 130 |  |  |  | 20 | 300 |  |  | 30 | 79 | 10 | 8,5 | 8,5