## Worksheet
Date of log | Subscriber's name | Date of measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-05-31 | NAVA AELOS | 2026-05-30 | 0,2 |  | 199 |  | 30 | 649 | 44 | 30 | 29 | 29 | 34 | 85 | 9,5 | 8,5 | 8,5
2026-05-31 | NAVA AELOS | 2026-05-29 | 0,2 |  | 249 |  | 30 | 670 | 38 | 30 | 35 | 36 | 35 | 85 | 8,5 | 8,5 | 8,5
2026-05-31 | NAVA AELOS | 2026-05-28 | 0,1 |  | 199 |  | 29 | 650 | 50 | 30 | 30 | 30 | 35 | 85 | 9,5 | 8,5 | 8,5
2026-05-31 | NAVA AELOS | 2026-05-27 | 0,2 |  | 169 |  | 29 | 700 | 49 | 30 | 24 | 35 | 35 | 85 | 9,5 | 8,5 | 8,5
2026-05-31 | NAVA AELOS | 2026-05-26 | 0,1 |  | 200 |  | 30 | 650 | 49 | 23 | 30 | 30 | 35 | 85 | 9,5 | 8,5 | 8,5
2026-05-25 | NAVA AELOS | 2026-05-25 | 0,1 |  | 200 |  | 25 | 669 | 40 | 35 | 35 | 35 | 34 | 86 | 9,5 | 7,5 | 7,5
2026-05-25 | NAVA AELOS | 2026-05-24 | 0,1 |  | 199 |  | 25 | 649 | 40 | 37 | 38 | 25 | 32 | 85 | 9 | 8,5 | 8,5
2026-05-24 | NAVA AELOS | 2026-05-23 | 0,2 |  | 180 |  | 29 | 670 | 40 | 30 | 30 | 30 | 34 | 84 |  | 8 | 8,5
2026-05-24 | NAVA AELOS | 2026-05-22 | 0,2 |  | 199 |  | 30 | 648 | 39 | 30 | 40 | 40 | 35 | 85 | 9,5 | 8,5
2026-05-24 | NAVA AELOS | 2026-05-21 | 0,1 |  | 200 |  | 30 | 599 | 40 | 21 | 25 | 34 | 40 | 85 | 9,5 | 9 | 8,5
2026-05-24 | NAVA AELOS | 2026-05-20 | 0,2 |  | 199 |  | 29 | 600 | 50 | 36 | 40 | 34 | 40 | 85 | 8 | 9 | 8,5
2026-05-24 | NAVA AELOS | 2026-05-19 | 0,2 |  | 199 |  | 30 | 598 | 150 | 34 | 19 | 34 | 33 | 86 | 9 | 9 | 8,5
2026-05-18 | NAVA AELOS | 2026-05-18 | 0,15 |  | 219 |  | 29 | 677 | 49 | 30 | 29 | 31 | 40 | 85 | 8,5 | 9,0 | 8,5
2026-05-18 | NAVA AELOS | 2026-05-17 | 0,1 |  | 219 |  | 30 | 700 | 39 | 30 | 39 | 30 | 39 | 85 | 9,0 | 8,5 | 8,5
2026-05-18 | NAVA AELOS | 2026-05-16 | 0,1 |  | 229 |  | 29 | 598 | 100 | 26 | 24 | 30 | 29 | 85 | 9,0 | 8,5 | 8,5
2026-05-18 | NAVA AELOS | 2026-05-15 | 0,1 |  | 200 |  | 25 | 700 | 50 | 25 | 24 | 25 | 30 | 85 | 8 | 10 | 8,5
2026-05-18 | NAVA AELOS | 2026-05-14 | 0,2 |  | 249 |  | 24 | 600 | 99 | 35 | 24 | 27 | 24 | 85 | 10 | 9,0 | 9,0
2026-05-18 | NAVA ALOS | 2026-05-13 | 0,3 |  | 179 |  | 39 | 600 | 29 | 25 | 24 | 25 | 30 | 85 | 10 | 9 | 9
2026-05-18 | NAVA AELOS | 2026-05-12 | 0,3 |  | 210 |  | 39 | 699 | 39 | 25 | 25 | 25 | 34 | 85 | 10 | 9 | 9
2026-05-18 | NAVA AELOS | 2026-05-11 | 0,2 |  | 200 |  | 30 | 800 | 29 | 30 | 10 | 9 | 30 | 85 | 10 | 8,5 | 8,2
2026-05-10 | NAVA AELOS | 2026-05-10 | 0,3 |  | 200 |  | 20 | 750 | 30 | 25 | 2 | 9 | 44 | 85 | 11 | 8,5 | 8,5
2026-05-09 | NAVA AELOS | 2026-05-09 | 0,2 |  | 230 |  | 25 | 750 | 150 | 30 | 30 | 1 | 40 | 85 | 10 | 8,5 | 8,5
2026-05-08 | Nava Aeolos | 2026-05-08 | 0,2 |  | 200 |  | 30 | 800 | 30 | 20 | 0,4 | 100 | 40 | 90 | 10 | 9 | 8,5