## Worksheet
Date of log | Subscriber's name | Date of measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-06-01 | MARIANNE SCHULTE | 2026-05-30 | 0,12 |  | 210 |  |  | 660 | 10 | 200 | 0 |  | 15 | 82 | 9 | 9 | 9
2026-05-27 | MARIANNE SCHULTE | 2026-05-23 | 0,12 |  | 230 |  |  | 665 | 20 | 200 | 0 |  | 15 | 82 | 11 | 9 | 9
2026-05-16 | MARIANNE SCHULTE | 2026-05-16 | 0,12 |  | 210 |  |  | 650 | 20 | 200 | 0 |  | 15 | 81 | 10,8 | 9 | 9
2026-05-16 | MARIANNE SCHULTE | 2026-05-09 | 0,12 |  | 190 |  |  | 660 | 20 | 200 | 0 |  | 15 | 82 | 11 | 9 | 9