## Worksheet
Date of log | Subscriber's name | Date of measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-06-30 | NAVA AEOLOS | 2026-06-30 | 0,15 |  | 170 |  | 25 | 650 | 100 | 10 | 25 | 25 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-06-27 | NAVA AEOLOS | 2026-06-28 | 0,15 |  | 190 |  | 25 | 650 | 100 | 20 | 30 | 23 | 28 | 85 | 9,5 | 8,5 | 8,5
2026-06-27 | NAVA AEOLOS | 2026-06-26 | 0,12 |  | 200 |  | 25 | 650 | 100 | 25 | 25 | 25 | 25 | 85 | 9,5 | 8,5 | 8,5
2026-06-27 | NAVA AEOLOS | 2026-06-23 | 0,12 |  | 170 |  | 30 | 650 | 100 | 24 | 30 | 30 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-06-21 | NAVA AEOLOS | 2026-06-20 | 0,15 |  | 180 |  | 25 | 600 | 80 | 23 | 30 | 20 | 39 | 85 | 9,5 | 8,5 | 8,5
2026-06-21 | NAVA AEOLOS | 2026-06-17 | 0,15 |  | 180 |  | 25 | 650 | 70 | 30 | 35 | 30 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-06-21 | NAVA AEOLOS | 2026-06-14 | 0,14 |  | 185 |  | 30 | 600 | 80 | 21 | 35 | 35 | 35 | 85 | 9,5 | 8,5 | 8,5
2026-06-21 | NAVA AEOLOS | 2026-06-11 | 0,15 |  | 190 |  | 25 | 650 | 70 | 42 | 34 | 30 | 32 | 85 | 9,5 | 8,5 | 8,5
2026-06-21 | NAVA AEOLOS | 2026-06-08 | 0,2 |  | 180 |  | 25 | 600 | 30 | 20 | 20 | 24 | 35 | 85 | 9,5 | 8,5 | 8,5
2026-06-21 | NAVA AEOLOS | 2026-06-06 | 0,1 |  | 200 |  | 25 | 650 | 30 | 24 | 20 | 18 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-06-05 | NAVA AELOS | 2026-06-05 | 0,14 |  | 179 |  | 30 | 650 | 36 | 30 | 35 | 30 | 44 | 85 | 9,5 | 7,5 | 8,5
2026-06-05 | NAVA AELOS | 2026-06-04 | 0,14 |  | 169 |  | 30 | 640 | 39 | 30 | 35 | 35 | 38 | 85 | 9,5 | 8,5 | 7,5
2026-06-05 | NAVA AELOS | 2026-06-03 | 0,15 |  | 199 |  | 29 | 649 | 39 | 30 | 30 | 36 | 33 | 85 | 8,5 | 8,5 | 8,5
2026-06-05 | NAVA AELOS | 2026-06-02 | 0,15 |  | 199 |  | 29 | 650 | 99 | 35 | 30 | 30 | 34 | 85 | 9,5 | 8,5 | 8,5
2026-06-05 | NAVA AELOS | 2026-06-01 | 0,1 |  | 199 |  | 29 | 650 | 29 | 35 | 34 | 23 | 34 | 84 | 8,5 | 7,5 | 8,5