## Worksheet
Date of log | Subscriber's name | Date of measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-06-29 | Sergei Rozhmanov | 2026-06-29 | 0,16 |  | 190 |  |  |  | 40 | 20 | 20 |  |  | 96 | 10,5 | 9 | 8,7
2026-06-29 | Sergei Rozhmanov | 2026-06-27 | 0,16 |  | 190 |  |  |  | 40 | 20 | 20 |  |  | 96 | 10,5 | 9 | 8,7
2026-06-25 | Sergei Rozhmanov | 2026-06-25 | 0,16 |  | 190 |  |  |  | 40 | 20 | 20 |  |  | 96 | 10,5 | 9 | 8,7
2026-06-25 | Sergei Rozhmanov | 2026-06-23 | 0,16 |  | 190 |  |  |  | 40 | 20 | 20 |  |  | 90 | 10,5 | 9 | 8,7
2026-06-25 | Sergei Rozhmanov | 2026-06-21 | 0,16 |  | 190 |  |  |  | 40 | 20 | 20 |  |  | 90 | 10,5 | 9 | 8,7
2026-06-19 | Sergei Rozhmanov | 2026-06-19 | 0,16 |  | 190 |  |  |  | 40 | 20 | 20 |  |  | 90 | 10 | 9 | 8,7
2026-06-19 | Sergei Rozhmanov | 2026-06-17 | 0,16 |  | 170 |  |  |  | 40 | 20 | 20 |  | 60 | 90 | 10 | 9 | 8,7
2026-06-19 | SERGEI ROZHMANOV | 2026-06-15 | 0,16 |  | 170 |  |  |  | 40 | 20 | 20 |  | 60 | 90 | 9 | 9 | 8,7
2026-06-16 | Sergei Rozhmanov | 2026-06-15 | 0,16 |  | 190 |  |  |  | 20 | 20 | 20 |  | 60 | 90 | 10 | 9 | 8,7
2026-06-11 | Sergei Rozhmanov | 2026-06-11 | 0,16 |  | 190 |  |  |  | 20 | 20 | 20 |  |  | 85 | 10 | 9 | 8,7
2026-06-10 | Sergei Rozhmanov | 2026-06-09 | 0,16 |  | 170 |  |  |  | 20 | 20 | 20 |  | 60 | 85 | 10 | 9 | 8,5
2026-06-07 | Sergei Rozhmanov | 2026-06-07 | 0,16 |  | 170 |  |  |  | 40 | 20 | 20 |  | 60 | 85 | 10 | 9 | 8,5
2026-06-06 | Sergei Rozhmanov | 2026-06-05 | 0,16 |  | 170 |  |  |  | 40 | 20 | 20 |  | 60 | 85 | 10 | 9 | 8,5
2026-06-03 | Sergei Rozhmanov | 2026-06-03 | 0,16 |  | 170 |  |  |  | 40 | 20 | 20 |  | 60 | 85 | 10 | 9 | 8,5
2026-06-01 | ARMAH SETH | 2026-06-01 | 0,2 |  | 180 |  |  |  | 20 | 20 | 20 | 20 | 15 | 80 | 10,5 | 9 | 8,5