## Worksheet
Date | Subscriber's name | Daily measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-06-28 | Marko Braunovic | 2026-06-28 | 0,2 |  | 180 |  | 20 | 700 | 40 | 300 | 0 | 0 | 20 | 85 | 9,5 | 8,7 | 8,7
2026-06-21 | Marko Braunovic | 2026-06-21 | 0,2 |  | 180 |  | 20 | 700 | 40 | 300 | 0 | 0 | 20 | 85 | 9,5 | 8,7 | 8,5
2026-06-14 | Marko Braunovic | 2026-06-14 | 0,2 |  | 180 |  | 20 | 700 | 40 | 300 | 0 | 0 | 20 | 85 | 9,5 | 8,7 | 8,5
2026-06-06 | Marko Braunovic | 2026-06-06 | 0,2 |  | 180 |  | 20 | 700 | 40 | 300 | 0 | 0 | 20 | 84 | 9,5 | 8,5 | 8,5