## Worksheet
Date of log | Subscriber's name | Date of measurements | DEHA (Normal range 0.1 - 0.4) | OXYAMINE dosage in liters | P - Alkalinity in ppm. (Normal range 150-300 ppm) | FOS CONDENSAMINE dosage in liters | Phosphate in ppm | Neutralized conductivity μS/cm | Chloride ( normal range 0-200 ppm CI ) | Makeup water usage in ltr. | Chloride ( Makeup water ) in ppm (reference) | Hardness ( Makeup water ) in ppm (reference) | Blowdown (in sec) | Hotwell temperature (*C) | pH ( Boiler ) | pH ( Hotwell tank Boiler Feedwater normal range 8.5-9.5 ) | pH ( Condensate normal range 8.2-9.2 )
2026-07-30 | NAVA AEOLOS | 2026-07-30 | 0,14 |  | 250 |  | 30 | 650 | 145 | 21 | 13 | 23 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-07-30 | NAVA AEOLOS | 2026-07-28 | 0,14 |  | 2 | 260 | 30 | 650 | 100 | 30 | 23 | 30 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-07-26 | NAVA AEOLOS | 2026-07-25 | 0,15 |  | 250 |  | 30 | 700 | 123 | 34 | 23 | 34 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-07-22 | NAVA AELOS | 2026-07-22 | 0,14 |  | 265 |  | 30 | 700 | 120 | 13 | 30 | 16 | 50 | 85 | 10 | 9,5 | 8,5
2026-07-22 | NAVA AELOS | 2026-07-20 | 0,15 |  | 255 |  | 30 | 650 | 130 | 15 | 10 | 10 | 50 | 85 | 10 | 8,5 | 8,5
2026-07-22 | NAVA AEOLOS | 2026-07-17 | 0,15 |  | 260 |  | 35 | 700 | 150 | 20 | 23 | 30 | 56 | 85 | 9,5 | 8,5 | 8,5
2026-07-22 | NAVA AEOLOS | 2026-07-14 | 0,14 |  | 250 |  | 30 | 650 | 100 | 16 | 25 | 10 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-07-22 | NAVA AEOLOS | 2026-07-11 | 0,14 |  | 250 |  | 30 | 650 | 100 | 10 | 30 | 20 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-07-08 | NAVA AELOS | 2026-07-08 | 0,16 |  | 260 |  | 30 | 700 | 100 | 24 | 25 | 25 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-07-08 | NAVA AELOS | 2026-07-07 | 0,15 |  | 200 |  | 30 | 650 | 100 | 30 | 30 | 25 | 49 | 85 | 9,5 | 8,5 | 8,5
2026-07-08 | NAVA AEOLOS | 2026-07-04 | 0,1 |  | 170 |  | 30 | 650 | 100 | 25 | 25 | 25 | 45 | 85 | 9,5 | 8,5 | 8,5
2026-07-08 | NAVA AEOLOS | 2026-07-01 | 0,1 |  | 160 |  | 25 | 650 | 100 | 10 | 25 | 25 | 35 | 85 | 9,5 | 8,5 | 8,5